## State_Table
State_Label | Description | Temperature [K] | Pressure [Pa] | Carried_Energy_Rate [W] | Specific_Energy [J/kg] | Flow_Exergy_Rate [W] | Specific_Flow_Exergy [J/kg]
1 | Fan Inlet | 293.15 | 100000 | 11672473.8676 | 294615.75 | 0 | 0
2 | Fan Outlet | 307.1026 | 110000 | 12228029.4232 | 308638.0917 | 330516.4547 | 8342.3064
2B | 2B (Bet. heating by HE and HP) | 307.2804 | 110000 | 12235110.1777 | 308816.8114 | 330840.1106 | 8350.4755
3 | Heating by Furnace- Outlet | 309.15 | 110000 | 12309552.4345 | 310695.75 | 334478.5454 | 8442.3104
4 | Hospital Discharge | 297.15 | 297.15 | 11831743.5093 | 298635.75 | 1076.8241 | 27.1793

## exergy_sources_table
Sources of Exergy | Exergy Rate | Unit1 | Specific Exergy | Unit2
Exegy of Flow to Fan | 0 | W | 0 | kJ/kg
Exergy of Work Input to Fan | 555555.5556 | W | 14022.3417 | kJ/kg
Exergy of Heat Input to Furnace | 14269.4258 | W | 360.1634 | kJ/kg
Exergy of Heat Through HP | 0 | W | 0 | kJ/kg
Total Exergy Rate Input | 569824.9814 | W | 14382.505 | kJ/kg
Total Exergy Rate Input(Check) | 569824.9814 | W | 14382.505 | kJ/kg

## exergy_disposition_table
Exergy Disposition | Exergy Rate | Unit1 | Specific Exergy | Unit2
Useful Exergy by Hospital Distribution | 24728.9109 | W | 624.163 | kJ/kg
Exergy of Heat Loss by Furnace | 1426.9426 | W | 36.0163 | kJ/kg
Exergy of Heat Loss by HE | 0 | W | 0 | kJ/kg
Exergy of Flow Out at Hospital Exit | 1076.8241 | W | 27.1793 | kJ/kg
Exergy Destruction (Fan) | 225039.1008 | W | 5680.0353 | kJ/kg
Exergy Destruction (Furnace-Heating Whole) | 8880.3926 | W | 224.143 | kJ/kg
Exergy Destruction (Hospital) | 308672.8103 | W | 7790.9681 | kJ/kg
Total Exergy Rate Disposed | 569824.9814 | W | 14382.505 | kJ/kg
Total Exergy Rate Disposed(Check) | 569824.9814 | W | 14382.505 | kJ/kg

## SubSystems_Energy_Table
Subsystem (Components) | Power In [W] | Power Out [W] | Heat In [W] | Heat Out [W] | Heat Loss [W]
Fan | 555555.5556 | 0 | 0 | 0 | 0
The Whole Heating System by Furnace | 0 | 0 | 16429.1605 | 0 | 1642.9161
Hospital Air Distribution | 0 | 0 | 0 | 477808.9252 | 0

## SubSystems_Performance_Table
Subsystem (Components) | Entropy Production Rate [W/K] | Exergy Destruction Rate [W] | Energy Input Rate [W] | Energy Utilized Rate [W] | Energy Loss Rate [W] | Exergy Input Rate [W] | Exergy Utilized Rate [W] | Exergy Loss Rate [W] | Energy Utilization Efficiency [%] | Exergetic Efficiency [%]
Fan | 767.6585 | 225039.1008 | 555555.5556 | 555555.5556 | 0 | 555555.5556 | 330516.4547 | 0 | 100 | 59.493
The Whole Heating System by Furnace | 30.293 | 8880.3926 | 16429.1605 | 81523.0113 | 1642.9161 | 14269.4258 | 3962.0906 | 1426.9426 | 496.2092 | 27.7663
Hospital Air Distribution | 1052.9518 | 308672.8103 | 477808.9252 | 477808.9252 | 0 | 333401.7212 | 333401.7212 | 0 | 100 | 100

## SubSystems_Energy_Period_Table
Subsystem (Components) | Power In [J/period] | Power Out [J/period] | Heat In [J/period] | Heat Out [J/period] | Heat Loss [J/period]
Fan | 8.736e+12 | 0 | 0 | 0 | 0
The Whole Heating System by Furnace | 0 | 0 | 258345263695.3242 | 0 | 25834526369.5324
Hospital Air Distribution | 0 | 0 | 0 | 7.5134e+12 | 0

## SubSystems_Perform_Period_Table
Subsystem (Components) | Entropy Production [J/K-period] | Exergy Destruction [J/period] | Energy Input [J/period] | Energy Utilized [J/period] | Energy Loss [J/period] | Exergy Input [J/period] | Exergy Utilized [J/period] | Exergy Loss [J/period] | Energy Utilization Efficiency [%] | Exergetic Efficiency [%]
Fan | 12071276999.406 | 3.5387e+12 | 8.736e+12 | 8.736e+12 | 0 | 8.736e+12 | 5.1973e+12 | 0 | 100 | 59.493
The Whole Heating System by Furnace | 476351349.674 | 139642398156.9234 | 258345263695.3242 | 1.2819e+12 | 25834526369.5324 | 224383867259.3223 | 62303082376.4711 | 25834526369.5324 | 496.2092 | 27.7663
Hospital Air Distribution | 16557455936.8709 | 4.8538e+12 | 7.5134e+12 | 7.5134e+12 | 0 | 5.2427e+12 | 5.2427e+12 | 0 | 100 | 100

## The Whole System
System | Energy Efficiency/EUF [%] | Exergy Efficiency [%]
The Whole System | 83.5353 | 58.5095

## Cost_Table
Description | Cost [USD]
Electricity Cost for Fan (Winter) | 510085.3333
Fuel Cost for Heating by Furnace (Winter) | 5726.3955
Operator Cost (Winter) | 9500
Total Cost (without Equipment Financing Cost) (Winter) | 525311.7288
Fan Equipment Financing Cost (Winter) | 884.9208
Furnace Equipment Financing Costs (Winter) | 1327.3812
Additional CHEHP Equipment Financing Cost (Winter) | 13273.8123
Additional HeatExchanger Equipment Financing Cost (Winter) | 0
Total Cost (with Equipment Financing Cost) (Winter) | 540797.8432
Capital (Over its lifespan) Cost for Fan and Furnace | 25000
Additional Capital Cost (Over its lifespan) for Equipment (CHEHP & Heat Exchnager) | 150000

## Carbon_Emissions_Table_winter
Source System | Energy Input Units [kWh] | Fuel Input Volume [m3] | C02 emisssions [kg]
Fan | 2426666.6667 | 0 | 631571.6202
Furnace | 0 | 6968.3677 | 12771.8711