## State_Table
State_Label | Description | Temperature [K] | Pressure [Pa] | Carried_Energy_Rate [W] | Specific_Energy [J/kg] | Flow_Exergy_Rate [W] | Specific_Flow_Exergy [J/kg]
1 | Fan Inlet | 283.15 | 100000 | 11672473.8676 | 284565.75 | 0 | 0
2 | Fan Outlet | 296.6266 | 110000 | 12228029.4232 | 298109.7583 | 330516.4547 | 8057.7317
2A | 2A (After Heat Transfer from RegHE ) | 297.0453 | 110000 | 12245289.7547 | 298530.5517 | 331312.2601 | 8077.1328
2B | 2B (After heating by HE) | 298.6507 | 110000 | 12311470.9716 | 300143.9978 | 334577.9806 | 8156.7485
3 | 3 (After heating by HP) | 309.15 | 110000 | 12744288.5261 | 310695.75 | 364090.7229 | 8876.246
4 | 4-Hospital Discharge | 297.15 | 100000 | 12249604.8376 | 298635.75 | 13814.2383 | 336.7803
4A | 4A-Outlet of RegHE | 296.7313 | 100000 | 12232344.506 | 298214.9567 | 13012.629 | 317.2377

## exergy_sources_table
Sources of Exergy | Exergy Rate | Unit1 | Specific Exergy | Unit2
Exegy of Flow to Fan | 0 | W | 0 | kJ/kg
Exergy of Work Input to Fan | 555555.5556 | W | 13544.0083 | kJ/kg
Exergy of Heat Input to Furnace | 134817.1679 | W | 3286.7367 | kJ/kg
Exergy of Heat Through HP | 0 | W | 0 | kJ/kg
Total Exergy Rate Input | 690372.7235 | W | 16830.7451 | kJ/kg
Total Exergy Rate Input(Check) | 690372.7235 | W | 16830.7451 | kJ/kg

## exergy_disposition_table
Exergy Disposition | Exergy Rate | Unit1 | Specific Exergy | Unit2
Useful Exergy by Hospital Distribution | 41603.6743 | W | 1014.2649 | kJ/kg
Exergy of Heat Loss by Furnace | 13481.7168 | W | 328.6737 | kJ/kg
Exergy of Heat Loss by HE | 0 | W | 0 | kJ/kg
Exergy of Flow Out from Hospital (at exit of RegHE) | 13012.629 | W | 317.2377 | kJ/kg
Exergy Destruction (Fan) | 225039.1008 | W | 5486.2766 | kJ/kg
Exergy Destruction (Furnace-Heating Whole) | 88562.7923 | W | 2159.0914 | kJ/kg
Exergy Destruction (Hospital) | 308672.8103 | W | 7525.2008 | kJ/kg
Total Exergy Rate Disposed | 690372.7235 | W | 16830.7451 | kJ/kg
Total Exergy Rate Disposed(Check) | 690372.7235 | W | 16830.7451 | kJ/kg

## SubSystems_Energy_Table
Subsystem (Components) | Power In [W] | Power Out [W] | Heat In [W] | Heat Out [W] | Heat Loss [W]
Fan | 555555.5556 | 0 | 0 | 0 | 0
The Whole Heating System by Furnace | 0 | 0 | 154424.9863 | 0 | 15442.4986
Hospital Air Distribution | 0 | 0 | 0 | 494683.6885 | 0

## SubSystems_Performance_Table
Subsystem (Components) | Entropy Production Rate [W/K] | Exergy Destruction Rate [W] | Energy Input Rate [W] | Energy Utilized Rate [W] | Energy Loss Rate [W] | Exergy Input Rate [W] | Exergy Utilized Rate [W] | Exergy Loss Rate [W] | Energy Utilization Efficiency [%] | Exergetic Efficiency [%]
Fan | 794.7699 | 225039.1008 | 555555.5556 | 555555.5556 | 0 | 555555.5556 | 330516.4547 | 0 | 100 | 59.493
The Whole Heating System by Furnace | 312.7769 | 88562.7923 | 154424.9863 | 516259.103 | 15442.4986 | 134817.1679 | 32772.6588 | 13481.7168 | 334.3106 | 24.309
Hospital Air Distribution | 1090.1388 | 308672.8103 | 494683.6885 | 494683.6885 | 0 | 350276.4846 | 350276.4846 | 0 | 100 | 100

## SubSystems_Energy_Period_Table
Subsystem (Components) | Power In [J/period] | Power Out [J/period] | Heat In [J/period] | Heat Out [J/period] | Heat Loss [J/period]
Fan | 8.736e+12 | 0 | 0 | 0 | 0
The Whole Heating System by Furnace | 0 | 0 | 2.4283e+12 | 0 | 242830202396.3954
Hospital Air Distribution | 0 | 0 | 0 | 7.7788e+12 | 0

## SubSystems_Perform_Period_Table
Subsystem (Components) | Entropy Production [J/K-period] | Exergy Destruction [J/period] | Energy Input [J/period] | Energy Utilized [J/period] | Energy Loss [J/period] | Exergy Input [J/period] | Exergy Utilized [J/period] | Exergy Loss [J/period] | Energy Utilization Efficiency [%] | Exergetic Efficiency [%]
Fan | 12497597924.6897 | 3.5387e+12 | 8.736e+12 | 8.736e+12 | 0 | 8.736e+12 | 5.1973e+12 | 0 | 100 | 59.493
The Whole Heating System by Furnace | 4918354922.8488 | 1.3926e+12 | 2.4283e+12 | 8.1181e+12 | 242830202396.3954 | 2.12e+12 | 515343505756.2469 | 242830202396.3954 | 334.3106 | 24.309
Hospital Air Distribution | 17142215108.2243 | 4.8538e+12 | 7.7788e+12 | 7.7788e+12 | 0 | 5.508e+12 | 5.508e+12 | 0 | 100 | 100

## The Whole System
System | Energy Efficiency/EUF [%] | Exergy Efficiency [%]
The Whole System | 69.6757 | 50.7373

## Cost_Table
Description | Cost [USD]
Electricity Cost for Fan (Winter) | 510085.3333
Fuel Cost for Heating by Furnace (Winter) | 53824.9381
Operator Cost (Winter) | 9500
Total Cost (without Equipment Financing Cost) (Winter) | 573410.2714
Fan Equipment Financing Cost (Winter) | 884.9208
Furnace Equipment Financing Costs (Winter) | 1327.3812
Additional CHEHP Equipment Financing Cost (Winter) | 14158.7331
Additional HeatExchanger Equipment Financing Cost (Winter) | 884.9208
Total Cost (with Equipment Financing Cost) (Winter) | 590666.2274
Capital (Over its lifespan) Cost for Fan and Furnace | 25000
Additional Capital Cost (Over its lifespan) for Equipment (CHEHP & Heat Exchnager) | 160000

## Carbon_Emissions_Table_winter
Source System | Energy Input Units [kWh] | Fuel Input Volume [m3] | C02 emisssions [kg]
Fan | 2426666.6667 | 0 | 631571.6202
Furnace | 0 | 65498.7869 | 120048.496